## Introduction
Powering Parks Energy and Financial Modelling Tool
This tool was developed by Scene Connect, a low-carbon innovation consultancy and research organisation based in Edinburgh, London, and Liverpool. The Energy and Financial Modelling Tool tool comprises part of the Powering Parks project's replication toolkit. Funded by the National Lottery Community Fund, the National Lottery Heritage Fund and Nesta, Powering Parks has been developed in close collaboration with Hackney Council and Possible. Powering Parks seeks to identify, calculate, and capture the ambient heating potential of Hackney's public green spaces, unlocking low-carbon heating for the borough, helping contribute to London's carbon emission reductions targets, and potentially providing a new stream of revenue for the local authority.
Modelling Tool built by: |  | Louise Waters, Sebastian Michalski & Jim O'Donnell | Filled in by:
Version: |  | v1.1 | Version:
Date |  | 19th March 2020 | Date:
Primary Contact: |  | Alex Schlicke: alex.s@scene.community | Contact:
Heat Pump Energy and Financial Modelling Tool Instructions for Use This Energy and Financial Modelling Tool has been created to estimate the potential feasibility and the energy and cost savings of a ground-source heat pump (GSHP) project, and the effect of substituting it with electrical, gas or oil heating systems. It has been designed for a user working on behalf of a Local Authority or Council, and who has a basic technological understanding of heat pumps, their relevant input variables, and the basic environmental and financial measures of project benefits. The Tool’s primary output is an estimate of the heating resource density of the area in consideration. The Tool can also provide financial estimations, namely the capital cost investment (CAPEX) of the project and various economic indicators including Revenue, Simple Payback time, the Nominal Internal Rate of Return (IRR) and the 20-year Net Present Value. The User should interact with the Tool via the 'Tool Interface' tab in this Excel sheet only.
Model Inputs
1. Heat collector: Choose the pump type from the two available options: Vertical (a heat exchanger fitted into borehole) or Horizontal (a coiled loop running along a shallow trench).
2. Ground Conductivity and Temperature: some pre-defined, recommended values for each input will automatically appear. However, you can input custom values by simply clicking the box and changing the figure, ensuring the figure remains within the defined range.
3. Heat load definition input: choose from the two available ways to define the relative use of the pump – these terms are explained in the toolkit:
1 | Capacity Factor: represents the difference between a pump’s actual output and its maximum output, over a period of time.
2 | Full Load Equivalent running hours (FLEQ): represents the difference between a pump’s actual annual usage, and its rated maximum output.
4. A recommended pre-defined value for Capacity factor or FLEQ hours will automatically appear. However, you can input custom values by simply clicking the box and changing the figure.
5. Type of query: you can define the purpose of your inquiry by choosing from two available options:
1 | General resource estimation – This is the default option. It will provide a basic output for the estimated Resource density.
See the result in the blue Outputs box on the right-hand side of the Tool Interface.
2 | Assessing a specific opportunity – This will lead to further input requirements below and produce more detailed results.
Continue to step 6 below.
6. Which of these quantities do you wish to base the estimate on? You can choose from among four options:
1 | Area of land available for the heat collector – The heat pump system will be designed to maximize heat output from the land available.
Continue to step 7 below.
2 | Total peak heat load of the building(s) – The size of the heat pump system will be limited to providing the maximum heat demand of the building which it is designed to supply.
Continue to step 7 below.
3 | Total annual heat load of the building(s) – The area required for the heat pump system will be estimated based on the building’s annual heat load, defined according to the selected Heat load definition input in Step 3.
Continue to step 7 below.
4 | None of the above – similarly to the ‘General resource estimation’ option in Step 5, this option provides a basic Resource density estimation.
See the result in the blue Outputs box on the right-hand side of the Tool Interface.
7. Current type of heating system: You can choose from among four options.
1 | Electric heating – Will compare the carbon emissions performance of the GSHP with a conventional electrical heating system.
2 | Oil Heating – Will compare the carbon emissions performance of the GSHP with a conventional oil heating system.
3 | Gas Heating – Will compare the carbon emissions performance of the GSHP with a conventional gas heating system.
4 | Air source heat pump - Will compare the carbon emissions performance of the GSHP with a conventional air heat pump.
Values for Annual Carbon Footprint reductions, Annual N2O emissions reductions, and Annual NxO reductions for oil and gas heating, will be presented in the blue Outputs box.
8. Is economic estimation needed?
Selecting Yes will lead to further financial input options in step 9 below.
9. Financial Inputs
1 | Wholesale electricity price - you may adjust this figure by simply clicking the box and entering a new figure (in £/kWh)
2 | Wholesale heating oil/gas price – if oil and gas heating systems were selected for comparison in step 7, an additional option will allow you to enter their wholesale prices. Electric heating and Air-source heat pumps will not have this additional option.
Model Outputs
1 | Heat Energy
• | Resource density (in Watts of heat available per M2 of land)
• | For vertical heat collectors, the approximate number of boreholes will be calculated.
• | For horizontal heat collectors, the length of the trench required will be calculated.
2 | Environmental outputs
• | Annual Carbon Footprint (in tonnes of CO2-equivalent)
• | Annual reduction of N20 emissions (in kg of CO2-equivalent)
• | Reduction of NOx (for oil and gas heating systems) (in kg of NOx)
3 | Financial Results
• | Annual net revenues relative to BAU
• | Capital cost relative to BAU
• | Simple payback
• | Nominal Internal Rate of Return (IRR)
• | Net Present Value (NPV) of 20-year project

## Tool Interface
INPUTS
| Heat collector type | Vertical |  |  | What is the area of available land? | 200 | m2
| Ground thermal conductivity (vertical) | 4 | W/mK
| Ground thermal conductivity (horizontal) | 1.5 | W/mK |  | What is the peak heat load? | 45 | kW
| Mean ground temperature (vertical) | 12 | °C
| Mean ground temperature (horizontal) | 12 | °C |  | What is the annual heat load? | 200000 | kWh
| Heat load definition input | Capacity factor
| Capacity factor | 30% |  | OUTPUTS
| FLEQ hours | 2000 | hours |  | Resource density | 122.7179 | W/m2
NB - schemes with land available < 3000m2 and/or heat load <200kW could have higher resource densities!
| Type of query | Assessing a specific opportunity |  |  | Length of trench for heat collector | 0 | metres
| Which of these quantities do you wish to base the estimate on? | Total peak heat load of the building(s) |  |  | Approximate number of boreholes | 5
| Current type of heating system | Gas Heating |  |  | Annual Carbon Footprint reduction | 17.4657 | tons of CO2 equivalent
[5 empty] | Annual reduction of N2O emission | -35.044 | kg of CO2 equivalent
| NOX class of gas boiler (Class 6 - Since December 2018) | Class 6 |  |  | Annual reduction of local NOX emission (up to) | 8.1372 | kg of NOX
| Is the economic estimation needed? | Yes
Financial results
Financial Inputs
[5 empty] | Annual net revenues relative to BAU | 6322.4175
| Wholesale electricity price | 0.124 | £/kWh
[5 empty] | Capital cost relative to BAU | 126254.4855
| Wholesale gas price | 0.023776 | £/kWh
[5 empty] | Simple payback | 18.7919 | Years
| Wholesale heating oil price | 0.05157 | £/kWh
[5 empty] | Nominal IRR | 2.521%
[5 empty] | NPV of 20-year project | 1560.1047

## Selector
Tool interface selections
Ground thermal conductivity | W/mK | 4
Mean ground temperature | C | 12
FLEQ |  | 2628
FLEQ rounded up |  | 3000
Vertices (Power per metre of pipe) | [5 empty] | Power per metre of pipe - sheet lookup
| 11 | 12.0001 | (Mean ground temperature) |  |  | Number = hours per year, Code SL for horizontal slinky, BH for standard vertical
4.5 | 49 | 53
3.5 | 43 | 46 |  |  |  | 3000BH
(Ground thermal conductivity) | [5 empty] | 3000BH | 6 | 7 | 8 | 9 | 10 | 11 | 12.0001 | 13 | 14 | 15.0001 | (Mean ground temperature)
W/mK | [5 empty] | 4.5 | 29 | 32 | 37 | 41 | 45 | 49 | 53 | 58 | 62 | 66
[6 empty] | 3.5 | 25 | 28 | 32 | 36 | 39 | 43 | 46 | 50 | 53 | 57
[6 empty] | 2.5 | 20 | 23 | 26 | 29 | 32 | 35 | 38 | 40 | 43 | 46
[6 empty] | 1.4999 | 14 | 16 | 18 | 21 | 23 | 25 | 27 | 29 | 31 | 33
[6 empty] | -0.0001 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | -0.0001 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
(Ground thermal conductivity)
Maximum power to be extracted | W/m | 49.4997
Assumptions
[6 empty] | Separation of trenches | m | 4
[6 empty] | Separation of boreholes | m | 12
[6 empty] | Depth of boreholes | m | 150
Resource density - horizontal or large vertical schemes | W/m2 | 72.187
Resource density multiplier - small vertical schemes |  | 1.7
Validation lookup lists (used in Tool Interface)
| Heat collector type |  | Heat load definition input |  | Type of query | 26 18: Quantities estimate is based on; 43 31: Current heating type |  | Is the economic estimation needed
| Vertical |  | Capacity factor |  | General resource estimation | 26 18: Area of land available for the heat collector; 43 31: Electric heating |  | Yes
| Horizontal |  | FLEQ |  | Assessing a specific opportunity | 26 18: Total peak heat load of the building(s); 43 31: Oil Heating |  | No
[9 empty] | Total annual heat load of the building(s) | [5 empty] | Gas Heating
[9 empty] | None of the above | [5 empty] | Air source heat pump
Source: UK Government GHG Conversion Factors for Company Reporting 2019
Domestic heating fuel type | kg GHG per kWh energy consumed |  | Logic |  |  | 20 14: Boilers efficiency
Domestic electric heating | 0.2556 | 0 | bar: 20 14 to 26 18
Oil | 0.25974 | 0 | Vertical | 136589.3343 | NET!! | 20 14: 0.97; 26 18: source; 29 21: http://www.nef.org.uk/knowledge-hub/view/oil-central-heating
Mains gas | 0.18385 | 0.19559 | Horizontal | 0 | Gross | 20 14: 0.94; 26 18: source; 29 21: https://www.boilerguide.co.uk/articles/erp-boiler-efficiency-explained
Air source heat pump | 0.084899 | 0 |  | 136589.3343
Ground source heat pump | 0.067715 | 0.19559
Source: UK Government GHG Conversion Factors for Company Reporting 2019 | [5 empty] | 26 18: 10
Domestic heating fuel type | kg of local NOx per kWh energy consumed |  |  |  | Logic selector |  |  |  | 10 | 11 | 12 | 13 | 14 | 15
Domestic electric heating | 0 | 0 | [6 empty] | Class 1 | Class 2 | Class 3 | Class 4 | Class 5 | Class 6
Oil | 0.00012 | 0 | NET!! |  | 120 | 1000000 |  | Oil Heating | 1 | 1 | 1 | 1 | 1 | 120 |  | mg/kWh |  | 56
Mains gas | 5.6e-05 | 5.9574e-05 | Gross |  | 56 | 1000000 |  | Gas Heating | 233.9975 | 179.998 | 134.9985 | 89.999 | 62.9993 | 56 |  | mg/kWh |  | 57
Air source heat pump | 0 | 0
Ground source heat pump | 0 | 5.9574e-05 | [5 empty] | 57 | 10 10 Class 1: 15; 10 11 Class 2: $O$57; 10 12 Class 3: 56
Source: UK Government GHG Conversion Factors for Company Reporting 2019 | [17 empty] | 60
Domestic heating fuel type | kg NOxn per kWh energy consumed
Domestic electric heating | 0.00137 | 0
Oil | 0.00064 | 0 | NET!!
Mains gas | 0.0001 | 0.00010638 | Gross
Air source heat pump | 0.00045505 | 0
Ground source heat pump | 0.00036295 | 0.00010638
https://www.isoenergy.co.uk/latest-news/isoenergy-news/carbon-savings-from-a-heat-pump
Domestic heating fuel type | kg Carbon per kWh energy consumed
Domestic electric heating | 0.283
Oil | 0.268
Mains gas | 0.184
Air source heat pump | 0.094 |  | 3.0106
Ground source heat pump | 0.071 |  | 3.7746
This is where I played around with boreholes on smaller bits of land (where you can fit more in per m2) It's quite unscientific! Just aiming for some sensible multiplication factors that users can apply to work out areas required or heat available. |  |  |  | m2 of land | # of boreholes | area for one borehole | ratio of area per borehole compared to large schemes | <-- plotting with formulae | 10 10 Class 1: kW heat output
|  |  |  | 100 | 2 | 0.02 |  |  | 10 10 Class 1: 20.7899
|  |  |  | 200 | 4 | 0.02 | 2.963 | 2.9 | 10 10 Class 1: 41.5797
|  |  |  | 300 | 5 | 0.016667 | 2.4691 | 2.35 | 10 10 Class 1: 51.9746
|  |  |  | 400 | 5 | 0.0125 | 1.8519 | 1.8 | 10 10 Class 1: 51.9746
|  |  |  | 500 | 6 | 0.012 | 1.7778 | 1.715 | 10 10 Class 1: 62.3696
|  |  |  | 600 | 7 | 0.011667 | 1.7284 | 1.7 | 10 10 Class 1: 72.7645
|  |  |  | 700 | 8 | 0.011429 | 1.6931 | 1.685 | 10 10 Class 1: 83.1594
|  |  |  | 800 | 9 | 0.01125 | 1.6667 | 1.67 | 10 10 Class 1: 93.5543
|  |  |  | 900 | 10 | 0.011111 | 1.6461 | 1.655 | 10 10 Class 1: 103.9493
|  |  |  | 1000 | 11 | 0.011 | 1.6296 | 1.64 | 10 10 Class 1: 114.3442
|  |  |  | 1100 | 12 | 0.010909 | 1.6162 | 1.625 | 10 10 Class 1: 124.7391
|  |  |  | 1200 | 13 | 0.010833 | 1.6049 | 1.61 | 10 10 Class 1: 135.134
|  |  |  | 1300 | 14 | 0.010769 | 1.5954 | 1.595 | 10 10 Class 1: 145.529
|  |  |  | 1400 | 15 | 0.010714 | 1.5873 | 1.58 | 10 10 Class 1: 155.9239
|  |  |  | 1500 | 16 | 0.010667 | 1.5802 | 1.565 | 10 10 Class 1: 166.3188
|  |  |  | 1600 | 17 | 0.010625 | 1.5741 | 1.55 | 10 10 Class 1: 176.7138
|  |  |  | 1700 | 18 | 0.010588 | 1.5686 | 1.535 | 10 10 Class 1: 187.1087
|  |  |  | 1800 | 19 | 0.010556 | 1.5638 | 1.52 | 10 10 Class 1: 197.5036
|  |  |  | 1900 | 20 | 0.010526 | 1.5595 | 1.505 | 10 10 Class 1: 207.8985
|  |  |  | 2000 | 21 | 0.0105 | 1.5556 | 1.49 | 10 10 Class 1: 218.2935
|  |  |  | 2500 | 25 | 0.01 | 1.4815 | 1.415 | 10 10 Class 1: 259.8732
|  |  |  | 3000 | 25 | 0.0083333 | 1.2346 | 1.24 | 10 10 Class 1: 259.8732
|  |  |  | 3500 | 26 | 0.0074286 | 1.1005 | 1.08 | 10 10 Class 1: 270.2681
|  |  |  | 3750 | 26 | 0.0069333 | 1.0272 | 1 | 10 10 Class 1: 270.2681
|  |  |  | 4000 | 27 | 0.00675 | 1 | 1 | 10 10 Class 1: 280.663

## Financial integrator Tech Det
To match Word document:
Option 1: Supply 90% of school’s heat via borehole collectors
Feature |  |  | Notes | Check calc: |  | Check order
Number of boreholes |  | 5 |  |  |  | 1
Depth of boreholes | metres | 150 |  |  |  | 2
Ground collector peak capacity | kW | 37.1247 |  |  |  | 8
Heat Pump peak load COP |  | 3.1 | Full loading of system under worst seasonal conditions: 55°C building heating outlet temperature; 0°C ground loop temperature. | 55.5 | W/m with 1200 FLEQ run hours | 6 | A constant
System heating capacity | kW | 54.8032 |  |  |  | 7
Ground collector maximum annual extraction | kWh | 97563.8102 |  |  |  | 5 | Re-uses calculated "sys max annual heat supply"
Heat Pump seasonal coefficient of performance (SCOP) |  | 3.5 | Assuming weather-compensated system; conservative underlying assumptions regarding seasonal ground loop temperatures. |  |  | 3 | A constant
System maximum annual heat supply | kWh | 136589.3343 |  |  |  | 4
Total annual heat demand of facility | kWh | 136589.3343 |  |  |  | 9 | To calculate other heating system energy requirement
Heat pump capacity (approximate) | kW | 51.9746 |  |  |  | 10 | Electrical load of pump
Length of trenching for distribution pipework | metres | 170 | Pipes connecting boreholes and buildings should be buried in trenches at least 600mm deep. |  |  | 11
Option 2: Supply 90% of school’s heat via horizontal collectors
Feature |  |  | Notes | Check calc:
Area for heat collection | m2 | 0
Length of trenches for heat collection | metres | 0
Depth of trenches for heat collection | metres | 1
Length of pipe laid in trenches for heat collection | metres | 0
Ground collector peak capacity | kW | 0
Heat Pump peak load COP |  | 3.1 | Full loading of system under worst seasonal conditions: 55°C building heating outlet temperature; 0°C ground loop temperature.
System heating capacity | kW | 0
Ground collector maximum annual extraction | kWh | 0
Heat Pump seasonal coefficient of performance (SCOP) |  | 3.5 | Assuming weather-compensated system; conservative underlying assumptions regarding seasonal ground loop temperatures.
System maximum annual heat supply | kWh | 0
Total annual heat demand of school | kWh | 0
Heat pump capacity (approximate) | kW | 0
Length of trenching for distribution pipework | metres | 90 | Pipes connecting boreholes and buildings should be buried in trenches at least 600mm deep.

## GSHP CAPEX
| Vertical |  |  |  |  | Horizontal
| Specification & unit |  | No. | Cost per | Cost | Specification & unit |  | No. | Cost per | Cost
Design and project management |  |  | 1 | 6000 | 6000 |  |  | 1 | 6000 | 6000
Trenches | 170 | metres | 1 | 10200 | 10200 | 90 | metres | 1 | 4050 | 4050
Ground pipework | 340 | metres | 1 | 1700 | 1700 | 1180 | metres | 1 | 4720 | 4720
Site costs |  |  | 1 | 3000 | 3000 |  |  | 1 | 3000 | 3000 | Heat Pump exponent | 0.6
Boreholes | 150 | metres | 5 | 7200 | 36000 | [5 empty] | Reference Heat Pump power | 85 | kW
Heat Pump #1 | 51.9746 | kW | 1 | 22332.8812 | 22332.8812 | 0 | kW | 1 | 0 | 0 | Reference Heat Pump cost | 30000 | £
New building heating circulation pumps |  |  | 2 | 1488.8587 | 2977.7175 |  |  | 2 | 0 | 0 |  | 2000
New equipment for heating system retrofit |  |  | 100 | 148.8859 | 14888.5875 |  |  | 100 | 0 | 0 |  | 200
Installation and commissioning |  |  | 1 | 12655.2993 | 12655.2993 |  |  | 1 | 0 | 0 |  | 17000
BoP (manifold, ground loop fill, buffer tanks etc.) |  |  | 1 |  | 5500 |  |  | 1 |  | 900
Contingency |  |  |  |  | 11000 |  |  |  |  | 1800
Total |  |  |  |  | 126254.4855 |  |  |  |  | 20470
|  |  |  | Cost per kW | 2429.1559 |  |  |  | Cost per kW | #DIV/0!
Table 6: Indicative Capital Costs for Daubeney Fields Options 1 & 2
| Vertical | Horizontal
| Borehole collectors | Horizontal collectors
Design and project management | 6000 | 6000
Site costs | 3000 | 3000
Trenches and ground loop pipework | 11900 | 8800
Boreholes | 36000 | -
Heat Pumps | 22332.8812 | 0
New building heating circulation pumps | 2977.7175 | 0
New equipment for heating system retrofit | 14888.5875 | 0
Installation and commissioning | 12655.2993 | 0
Balance of Plant (manifold, ground loop fill, buffer tanks etc.) | 5500 | 900
Contingency | 11000 | 1800
Total | 126254.4855 | 20500

## Simple Payback
|  | Vertical | Horizontal | RESULT | Financial Parameters
Avoided costs |  |  |  |  | CPI (Annualised Inflation Rate for RHI, OPEX and equipment replacement costs)
RHI | [5 empty] | 2.5%
RHI Tier 1 heat generation | kWh/year | 68294.6672 | 0 | 68294.6672 | Annualised Inflation Rate for Energy Prices (+ Heat Sales) | 4%
RHI Tier 1 rate | £/kWh | 0.096408 | 0.096408 | 0.096408 | Discount Rate = WACC | 2.4%
RHI Tier 1 income | £/year | 6584.1523 | 0 | 6584.1523
RHI Tier 2 heat generation | kWh/year | 68294.6672 | 0 | 68294.6672
RHI Tier 2 rate | £/kWh | 0.028737 | 0.028737 | 0.028737
RHI Tier 2 income | £/year | 1962.5838 | 0 | 1962.5838
0
Heat sales |  |  |  | 0 | Copying energy prices from tool interface tab (£/kWh) |  | Cost of heat (£/kWh) | Efficiency/CoP
Heat consumption - school | kWh/year | 136589.3343 | 0 | 136589.3343 | Electric heating | 0.124 | 0 | 1
Heat price | £/kWh | 0.025294 | 0.025294 | 0.025294 | Oil heating | 0.05157 | 0 | 0.97
Revenue from heat sales | £/year | 3454.8464 | 0 | 3454.8464 | Gas heating | 0.023776 | 0.025294 | 0.94
|  |  |  | 0 | Air heatpump | 0.124 | 0 | 2.5 | https://www.adams-air.com/houston/what-is-COP.php
Avoided gas boiler maintenance and servicing cost | £/year | 900 | 900 | 900 |  |  | 0.025294
Operating costs
Heat pump electricity consumption
Heat pump SCOP |  | 3.5 | 3.5 | 3.5
Heat pump electricity consumption | kWh/year | 39025.5241 | 0 | 39025.5241
Electricity unit cost | £/kWh | 0.124 | 0.124 | 0.124
Heat pump electricity cost | £/year | -4839.165 | 0 | -4839.165
Non-energy costs
Heat pump annual maintenance and servicing cost | £/year | -1100 | -1100 | -1100
Administration: RHI reporting and heat billing | £/year | -640 | -640 | -640
Repeating assumptions from Heat Pump cost estimation in GSHP CAPEX tab
Net revenues |  |  |  |  | Capacity (kW) | Ref capacity (kW) | Cost modifier exponent
[5 empty] | 51.9746 | 85 | 0.6
Annual net revenues relative to BAU | £/year | 6322.4175 | -840 | 6322.4175
0
Capital cost relative to BAU |  | 126254.4855 | 20470 | 126254.4855 | Device replacement COST estimation | Replacement cost after 10 years for ref capacity (£) | Modified replacement cost after 10 years (£)
Avoided cost of gas boiler end-of-life replacements* |  | -7444.2937 | -10000 | -7444.2937 | Electric heating | -5000 | 0
Simple Payback excluding replacement costs | years | 18.7919 | -12.4643 | 18.7919 | Gas heating | -10000 | 0
|  |  |  | 0 | Oil heating | -10000 | -7444.2937
CO2 savings | tCO2e/year | 17.4657 | 17.4657 | 17.4657 | Air heatpump | -40000 | 0
NOx savings | kg/year | 8.1372 | 8.1372 | 8.1372 |  |  | -7444.2937

## Cashflow
Cashflow
Year of Project |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Income
Heat Sales to school |  |  | 3454.8464 | 3593.0402 | 3736.7618 | 3886.2323 | 4041.6816 | 4203.3488 | 4371.4828 | 4546.3421 | 4728.1958 | 4917.3236 | 5114.0166 | 5318.5772 | 5531.3203 | 5752.5731 | 5982.6761 | 6221.9831 | 6470.8624 | 6729.6969 | 6998.8848 | 7278.8402 | 7569.9938 | 7872.7936 | 8187.7053 | 8515.2135 | 8855.8221
RHI Tier 1 |  |  | 6584.1523 | 6748.7561 | 6917.475 | 7090.4119 | 7267.6722 | 7449.364 | 7635.5981 | 7826.488 | 8022.1502 | 8222.704 | 8428.2716 | 8638.9783 | 8854.9528 | 9076.3266 | 9303.2348 | 9535.8157 | 9774.2111 | 10018.5663 | 10269.0305 | 10525.7563 | 0 | 0 | 0 | 0 | 0
RHI Tier 2 |  |  | 1962.5838 | 2011.6484 | 2061.9397 | 2113.4881 | 2166.3254 | 2220.4835 | 2275.9956 | 2332.8955 | 2391.2178 | 2450.9983 | 2512.2733 | 2575.0801 | 2639.4571 | 2705.4435 | 2773.0796 | 2842.4066 | 2913.4668 | 2986.3034 | 3060.961 | 3137.485 | 0 | 0 | 0 | 0 | 0
Total Income |  | 0 | 12001.5825 | 12353.4447 | 12716.1765 | 13090.1323 | 13475.6791 | 13873.1963 | 14283.0764 | 14705.7256 | 15141.5639 | 15591.0259 | 16054.5614 | 16532.6357 | 17025.7302 | 17534.3433 | 18058.9905 | 18600.2054 | 19158.5402 | 19734.5667 | 20328.8763 | 20942.0815 | 7569.9938 | 7872.7936 | 8187.7053 | 8515.2135 | 8855.8221
Expenditure
Capital Expenditure |  | 0: 126254.4855
Electricity Costs |  |  | -4839.165 | -5032.7316 | -5234.0408 | -5443.4025 | -5661.1386 | -5887.5841 | -6123.0875 | -6368.011 | -6622.7314 | -6887.6407 | -7163.1463 | -7449.6722 | -7747.6591 | -8057.5654 | -8379.868 | -8715.0628 | -9063.6653 | -9426.2119 | -9803.2604 | -10195.3908 | -10603.2064 | -11027.3347 | -11468.428 | -11927.1652 | -12404.2518
OPEX |  |  | -1740 | -1783.5 | -1828.0875 | -1873.7897 | -1920.6344 | -1968.6503 | -2017.8665 | -2068.3132 | -2120.021 | -2173.0216 | -2227.3471 | -2283.0308 | -2340.1066 | -2398.6092 | -2458.5744 | -2520.0388 | -2583.0398 | -2647.6158 | -2713.8062 | -2781.6513 | -2851.1926 | -2922.4724 | -2995.5342 | -3070.4226 | -3147.1832
Reinvestment Fund
Total Expenditure |  | 126254.4855 | -6579.165 | -6816.2316 | -7062.1283 | -7317.1922 | -7581.773 | -7856.2344 | -8140.954 | -8436.3242 | -8742.7525 | -9060.6623 | -9390.4934 | -9732.703 | -10087.7656 | -10456.1746 | -10838.4425 | -11235.1016 | -11646.705 | -12073.8277 | -12517.0665 | -12977.0421 | -13454.399 | -13949.8071 | -14463.9623 | -14997.5877 | -15551.4349
Avoided Costs
Capital Expenditure |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9529.3254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPEX |  |  | 900 | 922.5 | 945.5625 | 969.2016 | 993.4316 | 1018.2674 | 1043.7241 | 1069.8172 | 1096.5626 | 1123.9767 | 1152.0761 | 1180.878 | 1210.3999 | 1240.6599 | 1271.6764 | 1303.4683 | 1336.0551 | 1369.4564 | 1403.6928 | 1438.7852 | 1474.7548 | 1511.6237 | 1549.4143 | 1588.1496 | 1627.8534
Total Avoided Costs |  | 0 | 900 | 922.5 | 945.5625 | 969.2016 | 993.4316 | 1018.2674 | 1043.7241 | 1069.8172 | 1096.5626 | 1123.9767 | 10681.4014 | 1180.878 | 1210.3999 | 1240.6599 | 1271.6764 | 1303.4683 | 1336.0551 | 1369.4564 | 1403.6928 | 1438.7852 | 1474.7548 | 1511.6237 | 1549.4143 | 1588.1496 | 1627.8534
Pre-finance Surplus |  | -126254.4855 | 6322.4175 | 6459.7131 | 6599.6106 | 6742.1417 | 6887.3377 | 7035.2293 | 7185.8465 | 7339.2186 | 7495.374 | 7654.3403 | 17345.4694 | 7980.8107 | 8148.3646 | 8318.8286 | 8492.2244 | 8668.5721 | 8847.8903 | 9030.1955 | 9215.5026 | 9403.8246 | -4409.6504 | -4565.3898 | -4726.8427 | -4894.2246 | -5067.7595
Debt Service
Mortgage Style Amortisation Payments - Funder 1 | 0
Mortgage Style Amortisation Payments - Funder 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Financial Expdenditure |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | -6579.165 | -6816.2316 | -7062.1283 | -7317.1922 | -7581.773 | -7856.2344 | -8140.954 | -8436.3242 | -8742.7525 | -9060.6623 | -9390.4934 | -9732.703 | -10087.7656 | -10456.1746 | -10838.4425 | -11235.1016 | -11646.705 | -12073.8277 | -12517.0665 | -12977.0421 | -13454.399 | -13949.8071 | -14463.9623 | -14997.5877 | -15551.4349
Cash Flow Before Tax |  | -126254.4855 | 6322.4175 | 6459.7131 | 6599.6106 | 6742.1417 | 6887.3377 | 7035.2293 | 7185.8465 | 7339.2186 | 7495.374 | 7654.3403 | 17345.4694 | 7980.8107 | 8148.3646 | 8318.8286 | 8492.2244 | 8668.5721 | 8847.8903 | 9030.1955 | 9215.5026 | 9403.8246 | -4409.6504 | -4565.3898 | -4726.8427 | -4894.2246 | -5067.7595
Capital Allowance / Depreciation | 80%
Corporation Tax Paid | 0%
Cash Flow After Tax |  | -126254.4855 | 6322.4175 | 6459.7131 | 6599.6106 | 6742.1417 | 6887.3377 | 7035.2293 | 7185.8465 | 7339.2186 | 7495.374 | 7654.3403 | 17345.4694 | 7980.8107 | 8148.3646 | 8318.8286 | 8492.2244 | 8668.5721 | 8847.8903 | 9030.1955 | 9215.5026 | 9403.8246 | -4409.6504 | -4565.3898 | -4726.8427 | -4894.2246 | -5067.7595
Cumulative Cash Flow |  | -126254.4855 | -119932.068 | -113472.3549 | -106872.7443 | -100130.6026 | -93243.2649 | -86208.0357 | -79022.1892 | -71682.9706 | -64187.5967 | -56533.2564 | -39187.7869 | -31206.9762 | -23058.6117 | -14739.7831 | -6247.5587 | 2421.0135 | 11268.9037 | 20299.0992 | 29514.6018 | 38918.4264 | 34508.776 | 29943.3861 | 25216.5434 | 20322.3188 | 15254.5593
Discounted Cash Flow |  | -126254.4855 | 6174.2358 | 6160.4625 | 6146.3663 | 6131.9421 | 6117.1847 | 6102.0887 | 6086.6487 | 6070.8593 | 6054.7149 | 6038.2098 | 13362.4636 | 6004.0947 | 5986.4728 | 5968.4668 | 5950.0705 | 5931.2778 | 5912.0822 | 5892.4775 | 5872.4571 | 5852.0144 | -2679.8166 | -2709.4355 | -2739.5053 | -2770.033 | -2801.0256
Cumulative Discounted Cash Flow |  | -126254.4855 | -120080.2497 | -113919.7872 | -107773.4208 | -101641.4787 | -95524.294 | -89422.2053 | -83335.5566 | -77264.6973 | -71209.9824 | -65171.7726 | -51809.309 | -45805.2144 | -39818.7416 | -33850.2748 | -27900.2042 | -21968.9265 | -16056.8443 | -10164.3668 | -4291.9097 | 1560.1047 | -1119.7119 | -3829.1475 | -6568.6528 | -9338.6857 | -12139.7114
- Capital allowance / depreciation - number in B27 is percentage of project cost that is for capital elements that are included in capital allowance calcs.
Nominal IRR | 2.521%
NPV of 20-year project | 1560.1047
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0
Financial Overview | Saving / Income / Cost per Unit (£/kWh) | 0: Annual Electricity Purchase/Used (MWh); 1: Annual Cost / Saving / Income; 2: Notes/Justifications
Exported Electricity (CfD) | 0.115 | 0: 77191.76; 1: 8877052.4
Exported Electricity (No CfD) | 0.045 | 0: 77191.76; 1: 3473629.2

## 1200BH
1200BH | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
4.5 | 37 | 41 | 47 | 52 | 57 | 62 | 67 | 72 | 77 | 83
3.5 | 33 | 37 | 42 | 47 | 51 | 56 | 61 | 65 | 69 | 74
2.5 | 28 | 32 | 36 | 40 | 43 | 47 | 51 | 55 | 59 | 63
1.5 | 21 | 24 | 27 | 30 | 33 | 36 | 39 | 42 | 45 | 48
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## 1800BH
1800BH | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
4.5 | 34 | 38 | 43 | 48 | 52 | 57 | 62 | 67 | 72 | 77
3.5 | 30 | 34 | 38 | 42 | 47 | 51 | 55 | 59 | 63 | 68
2.5 | 25 | 28 | 32 | 35 | 39 | 42 | 46 | 49 | 53 | 56
1.5 | 18 | 21 | 24 | 26 | 29 | 31 | 34 | 36 | 39 | 41
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## 2400BH
2400BH | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
4.5 | 31 | 35 | 40 | 44 | 48 | 53 | 57 | 62 | 66 | 71
3.5 | 27 | 31 | 35 | 39 | 43 | 46 | 50 | 54 | 58 | 62
2.5 | 22 | 25 | 29 | 32 | 35 | 38 | 41 | 44 | 47 | 51
1.5 | 16 | 18 | 21 | 23 | 25 | 27 | 30 | 32 | 34 | 37
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## 3000BH
3000BH | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
4.5 | 29 | 32 | 37 | 41 | 45 | 49 | 53 | 58 | 62 | 66
3.5 | 25 | 28 | 32 | 36 | 39 | 43 | 46 | 50 | 53 | 57
2.5 | 20 | 23 | 26 | 29 | 32 | 35 | 38 | 40 | 43 | 46
1.5 | 14 | 16 | 18 | 21 | 23 | 25 | 27 | 29 | 31 | 33
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## 3600BH
3600BH | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
4.5 | 29 | 32 | 37 | 41 | 45 | 49 | 53 | 58 | 61 | 66
3.5 | 25 | 28 | 32 | 35 | 39 | 43 | 46 | 49 | 53 | 57
2.5 | 20 | 23 | 26 | 29 | 32 | 34 | 37 | 40 | 43 | 46
1.5 | 14 | 16 | 18 | 21 | 22 | 24 | 26 | 28 | 30 | 32
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## 1200SL
1200SL | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
2.4 | 49 | 62 | 74 | 86 | 97 | 107 | 118 | #N/A | #N/A | #N/A
2 | 45 | 57 | 67 | 78 | 87 | 96 | 106 | #N/A | #N/A | #N/A
1.6 | 40 | 50 | 59 | 68 | 77 | 85 | 93 | #N/A | #N/A | #N/A
1.2 | 32 | 40 | 48 | 55 | 63 | 70 | 77 | #N/A | #N/A | #N/A
0.8 | 24 | 29 | 35 | 40 | 46 | 52 | 56 | #N/A | #N/A | #N/A
0.4 | 15 | 18 | 22 | 25 | 28 | 32 | 34 | #N/A | #N/A | #N/A

## 1800SL
1800SL | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
2.4 | 35 | 45 | 53 | 61 | 69 | 76 | 84 | #N/A | #N/A | #N/A
2 | 32 | 40 | 47 | 54 | 61 | 67 | 73 | #N/A | #N/A | #N/A
1.6 | 28 | 34 | 41 | 47 | 52 | 58 | 63 | #N/A | #N/A | #N/A
1.2 | 22 | 27 | 32 | 37 | 42 | 47 | 51 | #N/A | #N/A | #N/A
0.8 | 16 | 19 | 23 | 26 | 30 | 34 | 36 | #N/A | #N/A | #N/A
0.4 | 9.8 | 11 | 14 | 16 | 18 | 20 | 21 | #N/A | #N/A | #N/A

## 2400SL
2400SL | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
2.4 | 27 | 34 | 40 | 47 | 52 | 57 | 63 | #N/A | #N/A | #N/A
2 | 24 | 30 | 36 | 41 | 46 | 50 | 55 | #N/A | #N/A | #N/A
1.6 | 21 | 26 | 30 | 35 | 39 | 43 | 47 | #N/A | #N/A | #N/A
1.2 | 16 | 20 | 24 | 28 | 31 | 35 | 38 | #N/A | #N/A | #N/A
0.8 | 12 | 14 | 17 | 19 | 22 | 25 | 27 | #N/A | #N/A | #N/A
0.4 | 7 | 8.2 | 9.9 | 11 | 13 | 14 | 15 | #N/A | #N/A | #N/A

## 3000SL
3000SL | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
2.4 | 22 | 27 | 32 | 38 | 42 | 46 | 51 | #N/A | #N/A | #N/A
2 | 19 | 24 | 28 | 33 | 37 | 40 | 44 | #N/A | #N/A | #N/A
1.6 | 16 | 20 | 24 | 27 | 31 | 34 | 37 | #N/A | #N/A | #N/A
1.2 | 13 | 16 | 19 | 21 | 24 | 27 | 30 | #N/A | #N/A | #N/A
0.8 | 9 | 11 | 13 | 15 | 17 | 19 | 21 | #N/A | #N/A | #N/A
0.4 | 5.3 | 6.3 | 7.5 | 8.5 | 9.6 | 11 | 12 | #N/A | #N/A | #N/A

## 3600SL
3600SL | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
2.4 | 18 | 23 | 27 | 32 | 35 | 39 | 43 | #N/A | #N/A | #N/A
2 | 16 | 20 | 24 | 27 | 30 | 33 | 37 | #N/A | #N/A | #N/A
1.6 | 14 | 17 | 20 | 22 | 25 | 28 | 31 | #N/A | #N/A | #N/A
1.2 | 10 | 13 | 15 | 17 | 20 | 22 | 24 | #N/A | #N/A | #N/A
0.8 | 7.2 | 8.6 | 10 | 12 | 14 | 16 | 17 | #N/A | #N/A | #N/A
0.4 | 4.3 | 5 | 6 | 6.8 | 7.7 | 8.7 | 9.3 | #N/A | #N/A | #N/A